## DL580G2
Revision 0.97
Calculator:
| Input Line Voltage Vac | This System is Power Redundant
| Processor(s) | 1 | Processor(s) Selected
| Memory Boards Installed | 2 | Memory Board(s) Selected
| 128 MB Card(s) | 8 | 128 MB | Memory Card(s) Selected
| 256 MB Card(s) | 0 | 256 MB | Memory Card(s) Selected
| 512 MB Card(s) | 0 | 512 MB | Memory Card(s) Selected
| 1 GB Card(s) | 0 | 1 GB | Memory Card(s) Selected
| 2 GB Card(s) | 4 | 2 GB | Memory Card(s) Selected
Total of 12 Card(s) and 9 GB Memory selected.
| PCI Card(s) | 6 | PCI Card(s) Selected
| 9 GB HDD(s) | 4 | HDD(s) Selected
18 GB HDD(s)
36 GB HDD(s)
72 GB HDD(s)
|  | 0 | USB Ports Selected
Variable Load Dissipation:
|  | Total Current (amps) |  |  | Max Power (watts)
| For Development activity only: | +5V | +3.3V | +12V
| Available Currents and Total Watts ==> | 30 | 45 | 55 | 800
| Configured Currents and Total Watts ==> | 12.2 | 30.46 | 22.9529 | 460.4112
| Total System Input power requirement (W) | For reference only |  |  | 613.8816
| Total System Input current requirement (A) | UPS/PDU/Circuit Breaker Selection |  |  | 2.7235
| Total System BTU/Hr | Cooling/Airconditioning Calculation |  |  | 2093.3364
| Total System VA Rating | UPS Selection |  |  | 626.4098
| Total System Leakage Current (mA) | UPS/PDU/Circuit Breaker Selection |  |  | 2.0125
| Total System Peak Inrush Current (A) 2mS | UPS/PDU/Circuit Breaker Selection |  |  | 50
ProLiant DL580G2
Purpose:
The Proliant Power Calculators have two intended purposes:
1. Review the server loading to determine the number of power supplies required for the power supplies to be redundant. 2. Approximate the electrical and heat load per server for facilities planning.
Notes:
1. The Power Calculators are not intended to provide precise results due to too many variables involved. Where precise power electrical loads are required, measurements should be made on the actual hardware configured, as it will be used.
2. Final site installation of Compaq products must comply with all relevant national, state, municipal and local electrical and fire code requirements.
3. The maximum power and current ratings per power supply are listed in the Server Quick Specs.
4. Values shown are nominal values approximated from all Processors, Memories, HDD and PCI cards exercised at the same time. Measured values from idle systems will be a lot less.
Instruction:
1. Use drop-down menu to configure the system by selecting Line Input Voltage, number of Power Supplies, amount of Memory, number of Processors, Expansion Cards and Hard Drives.
2. Watch for error messages and correct as necessary.
- Intel Pentium® IV Xeon processor/s, Single to Quad
- 1MB to 2MB Level 2 Cache per CPU
- 6 Slots - 2 x 64-bit 66Mhz 'Hot Plug' PCI,
2 x 64-bit 33Mhz 'Hot Plug' PCI (1 available),
1 x 64-bit 33Mhz PCI(0 available), 1 x 32-bit 33Mhz PCI
- 6 Bays - 1x floppy, 1x CD, 4x Hot Plug Bays
- 32 GB memory max, DDRAM 133Mhz
- Integrated Smart Array Controller
- Embedded Compaq NC3163 Fast Ethernet (10/100MB)
- 1280 x 1024, 256 colour graphics, 2MB PCI bus based
- Hot Plug Fans, keyboard and mouse ports
- High Speed IDE CD-ROM Drive
- Insight Manager, SmartStart, IRC, ASR-2
- Supports Win NT, Win 2000, Netware, SCO, OS/2,
- Banyan Vines, Unixware and OpenServer.
- 800 watt Hot Plug power supply
- Dimensions 6.94 x 19 x 28.3in inc. handles & fan. 4U rack height
- Weight 66lbs
- 3 year warranty
Click Here for Power Calculator Catalog
Power Calculator Links:
Power Calculator Catalog has links to all the individual Power Calculator available. It also includes a link to the Site Preparation Utility which allows the configuration of a rack with various quantities of different types of servers.

## Data (hidden)
DL580 G2 Power Calculator for Quantum:
| Revision 0.97 | 2026-07-29
Calculator:
| Description |  | Current Each Item (amps) |  |  |  | Power | Total Current (amps) |  |  | Max Power (watts) | Remarks/Errors | Total Current (amps) |  |  | Max Power (Watts)
|  |  | +5V | +3.3V | +12V | 5Vaux |  | +5V | +3.3V | +12V |  |  | +5V | +3.3V | +12V
Power Available
| Input Line Voltage Vac | 2 | 30 | 45 | 55 | 5 | 800 | 30 | 45 | 55 | 800
|  | 2 | 30 | 45 | 55 | 5 | 800
| Total Power Available: | [6 empty] | 30 | 45 | 55 | 800 |  | 30 | 45 | 55 | 800
Power Required
Fixed Loads
| Power Backplane | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0
| Processor Board | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| Memory Boards (Included in variable load below) | 0 | 0 | 0 | 1.81 |  |  | 0 | 0 | 0 | 0
| Fan Control Board | 0 | 0.28 |  |  |  |  | 0 | 0 | 0 | 0
| System/IO Board | 1 | 4.48 | 4.16 | 0.7 | 3.3 |  | 4.48 | 4.16 | 0.7 | 45.151
| STP Board | 0 | 2.54 | 0.31 |  |  |  | 0 | 0 | 0 | 0
| HDD Backplane | 1 | 0.35 | 0.7 |  |  |  | 0.35 | 0.7 | 0 | 4.095
| 120 mm Fans 1" | 4 |  |  | 0.5 |  |  | 0 | 0 | 2 | 24.5
| 121 mm Fans 1" | 0 |  |  | 0.5 |  |  | 0 | 0 | 0 | 0
| 122 mm Fans 1.5" | 3 |  |  | 2 |  |  | 0 | 0 | 6 | 73.5
| Redundant 120mm Fans | 0 |  |  | 0.6 |  |  | 0 | 0 | 0 | 0
| CD ROM | 1 | 0.7 |  | 0.21 |  |  | 0.7 | 0 | 0.21 | 6.1425
| Floppy Disk Drive, 3.5" | 1 | 0.63 |  |  |  |  | 0.63 | 0 | 0 | 3.213
| Mouse | 1 | 0.17 |  |  |  |  | 0.17 | 0 | 0 | 0.867
| Keyboard | 1 | 0.17 |  |  |  |  | 0.17 | 0 | 0 | 0.867
| Other Aux5V & -12V loads | 1 | [8 empty] | 16.5
| Fixed Load Dissipation: | [6 empty] | 6.5 | 4.86 | 8.91 | 174.8355
Variable Loads
| Foster Processor (1 - 4) | 1 |  | 1 | 7.2917 |  |  | 0 | 1 | 7.2917 | 92.6229 | 1 | 1 | Processors installed
| Processor Speed | 2
| Memory Boards | 1 |  |  | 0.89 |  | 2 | 0 | 0 | 1.78 | 21.805 |  | 2 | Memory Board(s) Selected
| 128 MB Card(s) | 3 |  |  | 0.18906 |  | 8 | 0 | 0 | 1.5125 | 18.5281 |  | 8 | 128 MB | Card(s) Selected
| 256 MB Card(s) | 1 |  |  | 0.22344 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 256 MB | Card(s) Selected
| 512 MB Card(s) | 1 |  |  | 0.24063 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 512 MB | Card(s) Selected
| 1 GB Card(s) | 1 |  |  | 0.26469 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 1 GB | Card(s) Selected
| 2 GB Card(s) | 2 |  |  | 0.26469 |  | 4 | 0 | 0 | 1.0588 | 12.9697 |  | 4 | 2 GB | Card(s) Selected
Total of 12 Card(s) and 9 GB Memory selected.
| PCI Card(s) | 7 | 0.55 | 4.1 | 0 |  | 6 | 3.3 | 24.6 | 0 | 98.01 | 6 | 6 | PCI cards Installed
| 9 GB HDD(s) | 5 | 0.6 |  | 0.6 |  | 4 | 2.4 | 0 | 2.4 | 41.64 | 4 | 4 | HDD Installed
| 18 GB HDD(s) | 5 | 0.6 |  | 0.6 |  | 0 | 0 | 0 | 0 | 0
| 36 GB HDD(s) | 5 | 0.76 |  | 0.66 |  | 0 | 0 | 0 | 0 | 0
| 72 GB HDD(s) | 1 | 0.8 |  | 0.81 |  | 0 | 0 | 0 | 0 | 0
|  | 1 |  | 0.3 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | USB Installed
| Variable Load Dissipation: |  |  |  | 162.738 | 443.9112 |  | 5.7 | 25.6 | 14.0429 | 285.5757
| Total Power Required (Fixed+Variable) | [6 empty] | 12.2 | 30.46 | 22.9529 | 460.4112 |  | 12.2 | 30.46 | 22.9529 | 460.4112
| System Power Redundancy ? | [6 empty] | 17.8 | 14.54 | 32.0471 | 339.5888
[12 empty] | This System is Power Redundant | This System is Power Redundant
| Total System Input power requirement (W) | [9 empty] | 613.8816 | For reference only | For reference only |  |  | 613.8816
| Total System Input current requirement (A) |  |  | Efficiency | 0.75 | 230 | VAC Input Voltage selected above |  |  |  | 2.7235 | UPS/PDU/Circuit Breaker Selection | UPS/PDU/Circuit Breaker Selection |  |  | 2.7235
| Total System BTU/Hr | [9 empty] | 2093.3364 | Cooling/Airconditioning Calculation | Cooling/Airconditioning Calculation |  |  | 2093.3364
| Total System VA Rating |  |  | PFC | 0.98 | [5 empty] | 626.4098 | UPS Selection | UPS Selection |  |  | 626.4098
| Total System Leakage Current (mA) |  |  | Leakage Current | 2.0125 | [5 empty] | 2.0125 | UPS/PDU/Circuit Breaker Selection | UPS/PDU/Circuit Breaker Selection |  |  | 2.0125
| Total System Peak Inrush Current (A) 2mS |  |  | Inrush Current | 50 | [5 empty] | 50 | UPS/PDU/Circuit Breaker Selection | UPS/PDU/Circuit Breaker Selection |  |  | 50
8
| 0 |  | Efficiency | Leakage Current | Inrush Current |  |  |  | Equivalent 3.3V memory current in Amps
| 1 | 240 | 0.76 | 1.05 | 25 |  |  |  | 0.55
| 2 | 230 | 0.75 | 1.0063 | 25 |  |  |  | 0.65
| 3 | 220 | 0.75 | 0.9625 | 25 |  |  |  | 0.7
| 4 | 208 | 0.75 | 0.91 | 25 |  |  |  | 0.77
| 5 | 115 | 0.72 | 0.50313 | 25 |  |  |  | 0.77
| 6 | 100 | 0.7 | 0.4375 | 25
| 7 | 48VDC input voltage | 0 |  | 0
8
[7 empty] | Processor |  | Power
|  | 1 power supplies (Non Redundant Option) |  |  |  | 1.4 | 1.5 GHz or less |  | 56 | 56.25
|  | 2 power supplies (1+1 Redundant Option) |  |  |  | 1.6 | 1.7 GHz or higher |  | 70
[7 empty] | Full FMB spec |  | 86
|  | Max Cofiguration |  |  | 0 USB port | 1 Memory board
|  | Processor | 4 |  | 1 USB port | 2 Memory boards
|  | Memory Slots | 16 |  | 2 USB ports
|  | Mem Group | 4
|  | PCI | 6
|  | HDD | 4
|  | IB | 0
|  | IB |  | PCI | 9GB |  | 18GB | 36GB | 72 GB ULTRA320
|  | 0 |  | 6 | 4 |  | 0 | 0 | 0
|  |  |  | 6 |  |  | 0 | 0 | 0
|  | 0 | 6 | 0 | 0 | 4 | 0 | 0 | 0
|  | 1 | 4 | 1 | 1 | 3 | 0 | 0 | 0
|  | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0
|  | 3 | 0 | 3 | 3 | 1 | 0 | 0 | 0
|  | 4 | -2 | 4 | 4 | 0 | 0 | 0 | 0
|  | 5 | -4 | 5 | 5 | -1 | 0 | 0 | 0
|  | 6 | -6 | 6 | 6 | -2 | 0 | 0 | 0
|  | 7 | -8 | 6 | 7 | -3 | 0 | 0 | 0
|  | 8 | -10 | 6 | 8 | -4 | 0 | 0 | 0
|  | 9 | -12 | 6 | 9 | -5 | 0 | 0 | 0
|  | 10 | -14 | 6 | 10 | -6 | 0 | 0 | 0
|  | 11 | -16 | 6 | 11 | -7 | 0 | 0 | 0
|  | 12 | -18 | 6 | 12 | -8 | 0 | 0 | 0
[5 empty] | 128MB |  | 256 MB | 512 MB | 1 GB | 2 GB
[5 empty] | 0.125 |  | 0.25 | 0.5 | 1 | 2 | 9
[5 empty] | 8 |  | 0 | 0 | 0 | 4 | 12
[7 empty] | 8 | 8 | 8 | 8
|  |  |  | 0 | 0 | 16 | 0 | 0 | 0 | 0
|  |  |  | 1 | 4 | 12 | 4 | 4 | 4 | 4 | 2
|  |  |  | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 2
|  |  |  | 3 | 12 | 4 | 8 | 8 | 8 | 8
|  |  |  | 4 | 16 | 0 | 8 | 8 | 8 | 8
|  |  |  | 5 | 20 | -4 | 8 | 8 | 8 | 8
|  |  |  | 6 | 24 | -8 | 8 | 8 | 8 | 8
|  |  |  | 7 | 28 | -12 | 8 | 8 | 8 | 8
|  |  |  | 8 | 32 | -16 | 8 | 8 | 8 | 8
|  |  |  | 9 | 36 | -20 | 8 | 8 | 8 | 8
|  |  |  | 10 | 40 | -24 | 8 | 8 | 8 | 8
|  |  |  | 11 | 44 | -28 | 8 | 8 | 8 | 8
|  |  |  | 12 | 48 | -32 | 8 | 8 | 8 | 8
|  |  |  | 13 | 52 | -36 | 8 | 8 | 8 | 8
|  |  |  | 14 | 56 | -40 | 8 | 8 | 8 | 8
|  |  |  | 15 | 60 | -44 | 8 | 8 | 8 | 8
|  |  |  | 16 | 64 | -48 | 8 | 8 | 8 | 8
|  |  |  | 17 | 68 | -52 | 8 | 8 | 8 | 8
|  |  |  | 18 | 72 | -56 | 8 | 8 | 8 | 8
|  |  |  | 19 | 76 | -60 | 8 | 8 | 8 | 8
|  |  |  | 20 | 80 | -64 | 8 | 8 | 8 | 8
|  |  |  | 21 | 84 | -68 | 8 | 8 | 8 | 8
|  |  |  | 22 | 88 | -72 | 8 | 8 | 8 | 8
|  |  |  | 23 | 92 | -76 | 8 | 8 | 8 | 8
|  |  |  | 24 | 96 | -80 | 8 | 8 | 8 | 8
|  |  |  | 25 | 100 | -84 | 8 | 8 | 8 | 8
|  |  |  | 26 | 104 | -88 | 8 | 8 | 8 | 8
|  |  |  | 27 | 108 | -92 | 8 | 8 | 8 | 8
|  |  |  | 28 | 112 | -96 | 8 | 8 | 8 | 8
|  |  |  | 29 | 116 | -100 | 8 | 8 | 8 | 8
|  |  |  | 30 | 120 | -104 | 8 | 8 | 8 | 8
|  |  |  | 31 | 124 | -108 | 8 | 8 | 8 | 8
|  |  |  | 32 | 128 | -112 | 8 | 8 | 8 | 8
Note on D47: Estimated to be total 17W HDD
Note on D65: Measured value
Note on D71: Measured value
Note on D79: Max supported
Note on D80: Max supported
Note on D82: Max supported
Note on D83: Max supported
Note on D89: This column lists the max # PCI slots available corresponding to the # of IB selected. It sets up table for Vlookup.
Note on E65: Measured value
Note on E71: Measured value
Note on E88: Max # PCI slots available corresponding to the # of IB selected. From the table using Vlookup.
Note on E89: This column lists available selection up to the max PCI slots available corresponding to the # of IB selected.
Note on F31: SAirey: Includes VRM efficiency 72W for processor and 80% VRM efficiency
Note on F47: Estimated to be total 17W HDD
Note on F65: Measured value
Note on F71: Measured value
Note on G17: SAirey: 3.3V aux 4A and 80% efficient
Note on G89: This column lists the max # HDD remaining slots available corresponding to the # of 9GB selected. It sets up table for Vlookup.
Note on G108: This column lists the max # HDD remaining slots available corresponding to the # of 9GB selected. It sets up table for Vlookup.
Note on H88: Max # HDD remaining slots available corresponding to the # of 9GB selected. From the table using Vlookup.
Note on H89: This column lists available selection up to the max HDD slots available corresponding to the # of 9GB selected.
Note on H107: Max # HDD remaining slots available corresponding to the # of 9GB selected. From the table using Vlookup.
Note on H108: This column lists available selection up to the max HDD slots available corresponding to the # of 9GB selected.
Note on I88: Max # HDD remaining slots available corresponding to the # of 9GB and 18GB selected. From the table using Vlookup.
Note on I89: This column lists available selection up to the max HDD slots available corresponding to the # of 9GB and 18GB selected.
Note on I107: Max # HDD remaining slots available corresponding to the # of 9GB and 18GB selected. From the table using Vlookup.
Note on I108: This column lists available selection up to the max HDD slots available corresponding to the # of 9GB and 18GB selected.
Note on J74: Measured power in S/Slew
Note on J75: 80% of FMBS 86W
Note on J88: Max # HDD remaining slots available corresponding to the # of 9GB, 18GB and 36GB selected. From the table using Vlookup.
Note on J89: This column lists available selection up to the max HDD slots available corresponding to the # of 9GB, 18GB and 36GB selected.
Note on J107: Max # HDD remaining slots available corresponding to the # of 9GB, 18GB and 36GB selected. From the table using Vlookup.
Note on J108: This column lists available selection up to the max HDD slots available corresponding to the # of 9GB, 18GB and 36GB selected.

## Quick Spec (hidden)
Power Supply Specification | Part number |  | 192147-001
| Spare Kit |  | 278535-B21
Operational Input Voltage Range ( V rms ) | 90 - 264
Frequency Range (Nominal) ( Hz ) | 47 - 63 ( 50 / 60 )
Nominal Input Voltage ( Vrms ) | 100 | 115 | 208 | 220 | 230 | 240
Max Rated Output Wattage Rating | 800 | 800 | 800 | 800 | 800 | 800
Nominal Input Current ( A rms ) | 12.0301 | 10.1704 | 5.2329 | 4.9474 | 4.7323 | 4.4755
Max Rated Input Wattage Rating ( Watts ) | 1142.8571 | 1111.1111 | 1066.6667 | 1066.6667 | 1066.6667 | 1052.6316
Max. Rated VA (Volt-Amp) | 1203.0075 | 1169.5906 | 1088.4354 | 1088.4354 | 1088.4354 | 1074.1139
Efficiency ( % ) | 70 | 72 | 75 | 75 | 75 | 76
Power Factor | 0.95 |  | 0.98
Leakage Current ( mA ) | 0.43478 | 0.5 | 0.90435 | 0.95652 | 1 | 1.0435
Max. Inrush Current (A peak ) | 25 | 25 | 25 | 25 | 25 | 25
Max. Inrush Current duration ( mS ) | 20
System Specifications | Processor | Memory | HDD | PCI | PS
DL580 Fully Configured | 4 | 32 | 4 | 6 | 2
Nominal Input Voltage ( Vrms ) | 100 | 115 | 208 | 220 | 230 | 240
Fully Loaded System Input Wattage (W) | 1068 | 1068 | 1025 | 1025 | 1025 | 1012
Fully Loaded System Input Current ( A rms ) | 11.6 | 9.8 | 5 | 4.8 | 4.5 | 4.3
Fully Loaded System Thermal ( BTU-Hr ) | 3746 | 3642 | 3496 | 3496 | 3496 | 3450
Fully Loaded System VA ( Volt-Amp ) | 1156 | 1124 | 1046 | 1046 | 1046 | 1032
System Leakage with all power supplies loaded (mA) | 0.86957 | 1 | 1.8087 | 1.913 | 2 | 2.087
System Inrush Current with all power supplies loaded (A) | 50 | 50 | 50 | 50 | 50 | 50
Power cord requirements | Nema 5-15P to IEC320-C19
Option no. 235603-001 / Spare no: 237457-001
PDU Jumper Cord IEC320-C19 to IEC320-C20
Option no 295633-B21. / Spare no.: 295508-001
* - To review typical system power ratings use the Active Answers Power Calculator which is available via the online tool located at url:
http://activeanswers.compaq.com/aaconfiguratorcode/
To drill down to calculators:
- Click on : “ProLiant Servers”
- Click on the Server of interest. Example : DL580
- Click on : “Power Calculator” link. ( You may need to scroll down to see it )

## QuickSpec (hidden)
Power Supply Specification | Part number |  | 192147-001
| Spare Kit |  | 192201-001
Operational Input Voltage Range ( V rms ) | 90 - 264
Frequency Range (Nominal) ( Hz ) | 47 - 63 ( 50 / 60 )
Nominal Input Voltage ( Vrms ) | 100 | 115 | 208 | 220 | 230 | 240
Max Rated Output Wattage Rating | 800 | 800 | 800 | 800 | 800 | 800
Nominal Input Current ( A rms ) | 11.6618 | 9.859 | 5.2329 | 4.9474 | 4.7323 | 4.4755
Max Rated Input Wattage Rating ( Watts ) | 1142.8571 | 1111.1111 | 1066.6667 | 1066.6667 | 1066.6667 | 1052.6316
Max. Rated VA (Volt-Amp) | 1166.1808 | 1133.7868 | 1088.4354 | 1088.4354 | 1088.4354 | 1074.1139
Efficiency ( % ) | 70 | 72 | 75 | 75 | 75 | 76
Power Factor | 0.98
Leakage Current ( mA ) | 0.43478 | 0.5 | 0.90435 | 0.95652 | 1 | 1.0435
Max. Inrush Current (A peak ) | 25 | 25 | 25 | 25 | 25 | 25
Max. Inrush Current duration ( mS ) | 20
System Specifications | Processor | Memory | HDD | PCI | PS
DL550 Fully Configured * | 4 | 32 | 4 | 6 | 2
Nominal Input Voltage ( Vrms ) | 100 | 115 | 208 | 220 | 230 | 240
Fully Loaded System Input Wattage (W) | 996 | 969 | 930 | 930 | 930 | 918
Fully Loaded System Input Current ( A rms ) | 10.5 | 8.9 | 4.6 | 4.3 | 4.1 | 3.9
Fully Loaded System Thermal ( BTU-Hr ) | 3397 | 3303 | 3171 | 3171 | 3171 | 3129
Fully Loaded System VA ( Volt-Amp ) | 1049 | 1020 | 949 | 949 | 949 | 936
System Leakage with all power supplies loaded (mA) | 0.86957 | 1 | 1.8087 | 1.913 | 2 | 2.087
System Inrush Current with all power supplies loaded (A) | 50 | 50 | 50 | 50 | 50 | 50
Power cord requirements # | Nema 6-20P to IEC320-C19 Option no. 235604-001 / Spare no: 237458-001
PDU Jumper Cord IEC320-C19 to IEC320-C20 Option no 295633-B21. / Spare no.: 295508-001
* - To review typical system power ratings use the Active Answers Power Calculator which is available via the online tool located at url:
http://activeanswers.compaq.com/aaconfiguratorcode/
To drill down to calculators:
- Click on : “ProLiant Servers”
- Click on the Server of interest. Example : DL550
- Click on : “Power Calculator” link. ( You may need to scroll down to see it )
# - Power cords (C19 Cord Sets) | Normal | Plug | Power | Option | Option | Spares
| Server | Style | Cord | Kit | Kit | Kit
| Voltage |  | Part | Part | Part | Part
| (VAC) |  | Number | Number | Number | Number
|  |  |  | Qty. = 1 | Qty. = 25
PDU Jumper Cord IEC320-C19 to IEC320-C20 |  |  | 242867-001 | 295633-B21 |  | 295508-001
Country
Argentina | 220
Australia | 240 |  | 295511-001 |  | 295529-011 | 295547-011
Austria | 220-230 | EURO | 295477-001 |  | 295529-021 | 295547-002
Bahamas | 120 | 5-15P | 178968-001 | 235603-001 |  | 237457-001
Belgium | 220-230 | EURO | 295477-001 |  | 295529-021 | 295547-002
Brazil | 110-220 | 5-15P | 178968-001 | 235603-001 |  | 237457-001
Canada | 120 | 5-15P | 178968-001 | 235603-001 |  | 237457-001
CzRch Rep | 220-230 | EURO | 295477-001 |  | 295529-021 | 295547-002
Chile | 220 |  | 295511-001 |  | 295529-011 | 295547-011
Columbia | 110-220 | 5-15P | 178968-001 | 235603-001 |  | 237457-001
Denmark | 220-230
Dominican Republic | 110 | 5-15P | 178968-001 | 235603-001 |  | 237457-001
Finland | 220-230 | EURO | 295477-001 |  | 295529-021 | 295547-002
France | 220-231 | EURO | 295477-001 |  | 295529-021 | 295547-002
Germany | 220-232 | EURO | 295477-001 |  | 295529-021 | 295547-002
Greece | 220-233 | EURO | 295477-001 |  | 295529-021 | 295547-002
Hong Kong | 200 | UK (13A) | 295478-001 | 376876-001 | 295529-031 | 295547-031
Hungary | 220 | EURO | 295477-001 |  | 295529-021 | 295547-002
Indonesia | 220 | EURO | 295477-001 |  | 295529-021 | 295547-002
India | 220-250 |  | 295510-001 |  | 295529-AR1 | 295547-AR1
Israel | 230 |  | 191241-002 | 196820-BT1
Italy | 220-230 |  | 295553-001
Japan | 100
Korea, S | 220 | EURO | 295477-001 |  | 295529-021 | 295547-002
Mayaysia | 240 | UK (13A) | 295478-001 | 376876-001 | 295529-031 | 295547-031
Mexico | 127 | 5-15P | 178968-001 | 235603-001 |  | 237457-001
Middle East | 220 | EURO | 295477-001 |  | 295529-021 | 295547-002
Netherlands | 220-230 | EURO | 295477-001 |  | 295529-021 | 295547-002
New Zealand | 230 |  | 295511-001 |  | 295529-011 | 295547-011
Norway | 220-230 | EURO | 295477-001 |  | 295529-021 | 295547-002
Philippines | 115 | 5-15P | 178968-001 | 235603-001 |  | 237457-001
Poland | 220 | EURO | 295477-001 |  | 295529-021 | 295547-002
Portugal | 220-230 | EURO | 295477-001 |  | 295529-021 | 295547-002
PRC (China) | 220 |  | 295511-001 |  | 295529-011 | 295547-011
Puerto Rico | 120 | 5-15P | 178968-001 | 235603-001 |  | 237457-001
Russia | 220 | EURO | 295477-001 |  | 295529-021 | 295547-002
Saudi Arabia | 127-220
Singapore | 230 | UK (13A) | 295478-001 | 376876-001 | 295529-031 | 295547-031
South Africa | 220-250 |  | 295510-001 |  | 295529-AR1 | 295547-AR1
Spain | 220-230 | EURO | 295477-001 |  | 295529-021 | 295547-002
Sweden | 220-230 | EURO | 295477-001 |  | 295529-021 | 295547-002
Switzerland | 220-230
Taiwan | 110 | 5-15P | 178968-001 | 235603-001 |  | 237457-001
Thailand | 220 | EURO | 295477-001 |  | 295529-021 | 295547-002
UK & Ireland | 240 | UK (13A) | 295478-001 | 376876-001 | 295529-031 | 295547-031
United States | 120 | 5-15P | 178968-001 | 235603-001 |  | 237457-001
Venezuela | 120 | 5-15P | 178968-001 | 235603-001 |  | 237457-001