## ML750
Revision 0.8
Calculator:
Input Line Voltage Vac
This System is Power Redundant
| Pentium Processors | 8 | Processor(s) Selected
| Total Memory Up To | 16 | 1 GB | Memory Card(s) Selected
Type of memory cards
|  | 11 | PCI Card(s) Selected
|  | 21 | HDD, DLT and CD ROM Selected
Variable Load Dissipation:
| Total System Input power requirement (W) | For reference only |  |  | 1174.7421
| Total System Input current requirement (A) | UPS/PDU/Circuit Breaker Selection |  |  | 4.9947
| Total System BTU-Hr | Cooling/Airconditioning Calculation |  |  | 4005.8707
| Total System VA Rating | UPS Selection |  |  | 1198.7165
| Total System Leakage Current (mA) | UPS/PDU/Circuit Breaker Selection |  |  | 2.087
| Total System Peak Inrush Current (A) 2mS | UPS/PDU/Circuit Breaker Selection |  |  | 100
ProLiant ML750
- Intel Pentium III XEON 900, 700 MHz
- Up to Eight Pentium III Xeon processors
- 1M/2M L2 caches
- Up to 16GB of 100MHz, ECC SDRAM memory
- Redundant array controllers
- 14U Rack form factor
- Hot-plug, load-balancing redundant power supplies
- 21 internal 1" drives
- Hot-Plug Redundant Fans
Purpose:
The Proliant Power Calculators have two intended purposes:
1. Review the server loading to determine the number of power supplies required for the power supplies to be redundant. 2. Approximate the electrical and heat load per server for facilities planning.
Notes:
1. The Power Calculators are not intended to provide precise results due to too many variables involved. Where precise power electrical loads are required, measurements should be made on the actual hardware configured, as it will be used.
2. Final site installation of Compaq products must comply with all relevant national, state, municipal and local electrical and fire code requirements.
3. The maximum power and current ratings per power supply are listed in the Server Quick Specs.
4. Values shown are nominal values approximated from all Processors, Memories, HDD and PCI cards exercised at the same time. Measured values from idle systems will be a lot less.
Instruction:
1. Use drop-down menu to configure the system by selecting Line Input Voltage, number of Power Supplies, amount of Memory, number of Processors, Expansion Cards and Hard Drives.
2. Watch for error messages and correct as necessary.
Click Here for Power Calculator Catalog
Power Calculator Links:
Power Calculator Catalog has links to all the individual Power Calculator available. It also includes a link to the Site Preparation Utility which allows the configuration of a rack with various quantities of different types of servers.

## ML750 Data (hidden)
ML750 Pentium Power Calculator
| Revision 0.8 | 2026-07-29
Purpose:
The Proliant Power Calculators have two intended purposes:
1. Review the server loading to determine the number of power supplies required for the power supplies to be redundant. 2. Approximate the electrical and heat load per server for facilities planning.
Notes:
1. The Proliant Power Calculators are not intended to provide precise results. There are too many variables involved to provide precise results. Where precise power electrical loads are required, measurements should be made on the actual hardware, configured as it will be used. 2. Final site installation of Compaq products must comply with all relevant national, state, municipal and local electrical and fire code requirements. 3. The maximum power and current ratings per power supply are listed in the Server Quick Specs.
4. Values shown are nominal values approximated from all Processors, Memories, HDD and PCI cards excercised at the same time. Measured values from idle systems will be a lot less.
Instruction:
| 1. Use drop-down menu to configure the system by selecting Line Input Voltage, number of Power Supplies, amount of Memory, number of Processors, Expansion Cards and Hard Drives . 2. Watch for error messages and correct as nescessary. | [15 empty] | HIDE THESE COLUMNS
HIDE THESE COLUMNS
Calculator:
| Description |  | Current Each Item (amps) |  |  | Power | Total Current (amps) |  |  | Max Power (watts) | Remarks/Errors | Total Current (amps) |  |  | Max Power (Watts) | Hide These Rows
|  |  | +5V | +3.3V | +12V |  | +5V | +3.3V | +12V |  |  | +5V | +3.3V | +12V
Power Available
| Input Line Voltage Vac | 1 | 63 | 100 | 60 | 1150 | 63 | 100 | 60 | 1150
2
| Total Power Available: | [5 empty] | 126 | 200 | 120 | 2300 |  | 126 | 200 | 120 | 2300
Power Required
Fixed Loads
1 | Power Backplane |  | 0.5 |  |  |  | 0.5 | 0 | 0 | 2.55
1 | Processor Board |  | 1.55 | 2.1 | 0 |  | 1.55 | 2.1 | 0 | 14.835
1 | Memory Boards |  | 1 | 1 |  |  | 1 | 1 | 0 | 8.4
1 | Fan Control Board |  | 0.28 |  |  |  | 0.28 | 0 | 0 | 1.428
1 | IO Board |  | 1.3 | 4.5 |  |  | 1.3 | 4.5 | 0 | 21.48
0 | STP Board |  | 2.54 | 0.31 |  |  | 0 | 0 | 0 | 0
3 | HDD Backplane |  | 0.5 |  |  |  | 1.5 | 0 | 0 | 7.65
3 | 120 mm Fans |  |  |  | 0.8 |  | 0 | 0 | 2.4 | 29.4
2 | 92 mm Fans |  |  |  | 0.5 |  | 0 | 0 | 1 | 12.25
1 | CD ROM |  | 0.7 |  | 0.21 |  | 0.7 | 0 | 0.21 | 6.1425
1 | Floppy Disk Drive, 3.5" |  | 0.63 |  |  |  | 0.63 | 0 | 0 | 3.213
1 | Mouse |  | 0.17 |  |  |  | 0.17 | 0 | 0 | 0.867
1 | Keyboard |  | 0.17 |  |  |  | 0.17 | 0 | 0 | 0.867
1 | Aux5V, -5, & -12V loads | [8 empty] | 6
| Fixed Load Dissipation: | [5 empty] | 7.8 | 7.6 | 3.61 | 115.0825
Variable Loads
Input Line Voltage Vac
This System is Power Redundant
| Pentium Processors | 8 |  | 1 | 2.2857 |  | 0 | 8 | 18.2857 | 250.4 |  | 8 | Processor(s) Selected
| Pentium Speed | 2
1 GB
| Total Memory Up To | 19 |  | 0.77 |  | 16 | 0 | 12.32 | 0 | 40.656 | 16 | 16 | 1 GB | Memory Card(s) Selected
| Type of memory cards | 4 | 1 | 16 | 16 | 16
|  | 1 | 0.98 |  | 0.21 | 0 | 0 | 0 | 0 | 0 | [5 empty] | Hide These Rows
|  | 1 | 2.18 |  | 0.06 | 0 | 0 | 0 | 0 | 0
|  | 1 | 3 | 0.3 | 0.06 | 0 | 0 | 0 | 0 | 0
|  | 1 | 3.63 |  |  | 0 | 0 | 0 | 0 | 0
|  | 1 | 2.75 |  |  | 0 | 0 | 0 | 0 | 0
|  | 1 | 2.9412 |  |  | 0 | 0 | 0 | 0 | 0 | 11 | 11 | PCI cards Installed
|  | 12 | 0.98039 | 3.0303 |  | 11 | 10.7843 | 33.3333 | 0 | 165 |  | 11 | PCI Card(s) Selected
|  |  | HDD | 21 | PCI | 11
|  | 1 | 0.76 |  | 0.66 | 0 | 0 | 0 | 0 | 0
|  | 1 | 0.76 |  | 0.66 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | HDD, DLT and CD ROM Selected
|  | 22 | 0.76 |  | 0.66 | 21 | 15.96 | 0 | 13.86 | 251.181
|  | 1 | 0.6 |  | 0.6 | 0 | 0 | 0 | 0 | 0
|  |  | DLT | 1 | CD ROM | 3
|  | 1 | 3.1 |  | 1.5 | 0 | 0 | 0 | 0 | 0
|  | 1 | 0.7 |  | 0.21 | 0 | 0 | 0 | 0 | 0
| Variable Load Dissipation: | [5 empty] | 26.7443 | 53.6533 | 32.1457 | 707.237
| Total Power Required (Fixed+Variable) | [5 empty] | 34.5443 | 61.2533 | 35.7557 | 822.3195 |  | 34.5443 | 61.2533 | 35.7557 | 822.3195 | Hide These Rows
| System Power Redundancy ? | [5 empty] | 28.4557 | 38.7467 | 24.2443 | 327.6805
[11 empty] | This System is Power Redundant | This System is Power Redundant
| Total System Input power requirement (W) | [8 empty] | 1174.7421 | For reference only | For reference only |  |  | 1174.7421
| Total System Input current requirement (A) |  | Efficiency | 0.7 | 240 |  |  |  |  | 4.9947 | UPS/PDU/Circuit Breaker Selection | UPS/PDU/Circuit Breaker Selection |  |  | 4.9947
| Total System BTU/Hr | [8 empty] | 4005.8707 | Cooling/Airconditioning Calculation | Cooling/Airconditioning Calculation |  |  | 4005.8707
| Total System VA Rating |  | PFC | 0.98 | [5 empty] | 1198.7165 | UPS Selection | UPS Selection |  |  | 1198.7165
| Total System Leakage Current (mA) |  | Leakage current | 2.087 | [5 empty] | 2.087 | UPS/PDU/Circuit Breaker Selection | UPS/PDU/Circuit Breaker Selection |  |  | 2.087
| Total System Peak Inrush Current (A) 2mS |  | Inrush Current | 100 | [5 empty] | 100 | UPS/PDU/Circuit Breaker Selection | UPS/PDU/Circuit Breaker Selection |  |  | 100
|  |  | Efficiency | Leakage Current | Inrush Current |  |  | Memory type | Current
|  | 240 | 0.7 | 1.0435 | 50 |  |  | 128M cards | 0.55 | 128 MB
|  | 230 | 0.69 | 1 | 50 |  |  | 256M cards | 0.6 | 256 MB
|  | 220 | 0.68 | 0.95652 | 50 |  |  | 512M cards | 0.7 | 512 MB
|  | 208 | 0.67 | 0.90435 | 50 |  |  | 1G cards | 0.77 | 1 GB
|  | 115 | 0.66 | 0.5 | 50 |  |  | 2G cards |  | 2 GB
|  | 100 | 0.65 | 0.43478 | 50 |  |  |  |  | 3 GB
|  | 48VDC input voltage | 0 |  | 0 |  |  |  |  | 4 GB
5 GB
[7 empty] | Processor |  | Power | 6 GB
|  | 1 power supply (Non Redundant Option) |  |  |  |  | 733 MHz or less |  | 25 | 7 GB
|  | 2 power supplies (1+1 Redundant Option) |  |  |  |  | 900 MHz or higher |  | 28 | 8 GB
|  | 3 power supplies (2+1 Redundant Option) | [7 empty] | 9 GB
|  | Non-Hot Pluggable Power Supply (Fixed) | [7 empty] | 10 GB
11 GB
|  | Max Cofiguration |  |  | Power Supply rating |  |  |  |  | 12 GB
|  | Processor | 8 |  |  | 5V | 3.3V | 12V | Watts | 13 GB
|  | Memory | 16 |  | Fix Non-Hotplug |  |  |  |  | 14 GB
|  | PCI | 11 |  | High Line | 63 | 100 | 60 | 1150 | 15 GB
|  | HDD | 21 |  | Low Line | 32 | 18 | 20 | 500 | 16 GB
|  | 1 | 0 ISA Modem | 0 Smart Array 4200 Controller | 0 DLT Drive
|  | 2 | 1 ISA Modem | 1 Smart Array 4200 Controller | 1 DLT Drive
|  | 3 |  | 2 Smart Array 4200 Controller | 2 DLT Drive
|  | 4 | 0 PCI Remote Insight Board | 3 Smart Array 4200 Controller
|  | 5 | 1 PCI Remote Insight Board | 4 Smart Array 4200 Controller | 0 CD ROM
|  | 6 |  | 5 Smart Array 4200 Controller | 1 CD ROM
|  | 7 | 0 Smart Array 4250ES Controller | 6 Smart Array 4200 Controller | 2 CD ROM
|  | 8 | 1 Smart Array 4250ES Controller | 7 Smart Array 4200 Controller | 3 CD ROM
|  |  | 2 Smart Array 4250ES Controller | 8 Smart Array 4200 Controller | 4 CD ROM
9 Smart Array 4200 Controller
|  | 0 NC3131 Fast Enet NIC w/NC6132 Gbit Mod'l |  | 0 +5V PCI cards | 0 PCI cards | 0 HDD, 1.0'', 4.3GB | 0 HDD, 1.0'', 9GB | 0 HDD, 1.0'', 18GB | 0 HDD, 1.0'', 36GB
|  | 1 NC3131 Fast Enet NIC w/NC6132 Gbit Mod'l |  | 1 +5V PCI cards | 1 PCI cards | 1 HDD, 1.0'', 4.3GB | 1 HDD, 1.0'', 9GB | 1 HDD, 1.0'', 18GB | 1 HDD, 1.0'', 36GB
|  | 2 NC3131 Fast Enet NIC w/NC6132 Gbit Mod'l |  | 2 +5V PCI cards | 2 PCI cards | 2 HDD, 1.0'', 4.3GB | 2 HDD, 1.0'', 9GB | 2 HDD, 1.0'', 18GB | 2 HDD, 1.0'', 36GB
|  | 3 NC3131 Fast Enet NIC w/NC6132 Gbit Mod'l |  | 3 +5V PCI cards | 3 PCI cards | 3 HDD, 1.0'', 4.3GB | 3 HDD, 1.0'', 9GB | 3 HDD, 1.0'', 18GB | 3 HDD, 1.0'', 36GB
|  | 4 NC3131 Fast Enet NIC w/NC6132 Gbit Mod'l |  | 4 +5V PCI cards | 4 PCI cards | 4 HDD, 1.0'', 4.3GB | 4 HDD, 1.0'', 9GB | 4 HDD, 1.0'', 18GB | 4 HDD, 1.0'', 36GB
|  | 5 NC3131 Fast Enet NIC w/NC6132 Gbit Mod'l |  | 5 +5V PCI cards | 5 PCI cards | 5 HDD, 1.0'', 4.3GB | 5 HDD, 1.0'', 9GB | 5 HDD, 1.0'', 18GB | 5 HDD, 1.0'', 36GB
|  | 6 NC3131 Fast Enet NIC w/NC6132 Gbit Mod'l |  | 6 +5V PCI cards | 6 PCI cards | 6 HDD, 1.0'', 4.3GB | 6 HDD, 1.0'', 9GB | 6 HDD, 1.0'', 18GB | 6 HDD, 1.0'', 36GB
|  | 7 NC3131 Fast Enet NIC w/NC6132 Gbit Mod'l |  | 7 +5V PCI cards | 7 PCI cards | 7 HDD, 1.0'', 4.3GB | 7 HDD, 1.0'', 9GB | 7 HDD, 1.0'', 18GB | 7 HDD, 1.0'', 36GB
|  | 8 NC3131 Fast Enet NIC w/NC6132 Gbit Mod'l |  | 8 +5V PCI cards | 8 PCI cards | 8 HDD, 1.0'', 4.3GB | 8 HDD, 1.0'', 9GB | 8 HDD, 1.0'', 18GB | 8 HDD, 1.0'', 36GB
|  | 9 NC3131 Fast Enet NIC w/NC6132 Gbit Mod'l |  | 9 +5V PCI cards | 9 PCI cards | 9 HDD, 1.0'', 4.3GB | 9 HDD, 1.0'', 9GB | 9 HDD, 1.0'', 18GB | 9 HDD, 1.0'', 36GB
[5 empty] | 10 PCI cards | 10 HDD, 1.0'', 4.3GB | 10 HDD, 1.0'', 9GB | 10 HDD, 1.0'', 18GB | 10 HDD, 1.0'', 36GB
[5 empty] | 11 PCI cards | 11 HDD, 1.0'', 4.3GB | 11 HDD, 1.0'', 9GB | 11 HDD, 1.0'', 18GB | 11 HDD, 1.0'', 36GB
[6 empty] | 12 HDD, 1.0'', 4.3GB | 12 HDD, 1.0'', 9GB | 12 HDD, 1.0'', 18GB | 12 HDD, 1.0'', 36GB
[6 empty] | 13 HDD, 1.0'', 4.3GB | 13 HDD, 1.0'', 9GB | 13 HDD, 1.0'', 18GB | 13 HDD, 1.0'', 36GB
[6 empty] | 14 HDD, 1.0'', 4.3GB | 14 HDD, 1.0'', 9GB | 14 HDD, 1.0'', 18GB | 14 HDD, 1.0'', 36GB
[6 empty] | 15 HDD, 1.0'', 4.3GB | 15 HDD, 1.0'', 9GB | 15 HDD, 1.0'', 18GB | 15 HDD, 1.0'', 36GB
[6 empty] | 16 HDD, 1.0'', 4.3GB | 16 HDD, 1.0'', 9GB | 16 HDD, 1.0'', 18GB | 16 HDD, 1.0'', 36GB
[6 empty] | 17 HDD, 1.0'', 4.3GB | 17 HDD, 1.0'', 9GB | 17 HDD, 1.0'', 18GB | 17 HDD, 1.0'', 36GB
[6 empty] | 18 HDD, 1.0'', 4.3GB | 18 HDD, 1.0'', 9GB | 18 HDD, 1.0'', 18GB | 18 HDD, 1.0'', 36GB
[6 empty] | 19 HDD, 1.0'', 4.3GB | 19 HDD, 1.0'', 9GB | 19 HDD, 1.0'', 18GB | 19 HDD, 1.0'', 36GB
[6 empty] | 20 HDD, 1.0'', 4.3GB | 20 HDD, 1.0'', 9GB | 20 HDD, 1.0'', 18GB | 20 HDD, 1.0'', 36GB
[6 empty] | 21 HDD, 1.0'', 4.3GB | 21 HDD, 1.0'', 9GB | 21 HDD, 1.0'', 18GB | 21 HDD, 1.0'', 36GB
Note on D55: Measured data
Note on D76: Measured value
Note on D82: Measured value
Note on D91: Max supported
Note on D92: Max supported
Note on D93: Max supported
Note on D94: Max supported
Note on E76: Measured value
Note on E82: Measured value
Note on F55: Measured data
Note on F76: Measured value
Note on F82: Measured value
Note on G45: Number of available memory slots.
Note on J76: Measured current
Note on J77: Measured current
Note on J78: Measured current
Note on J79: Measured current
Note on J80: Measured current
Note on J85: Measured power
Note on J86: Measured power